# POWER FLOW CALCULATION METHODOLOGY

Complete Mathematical Formulations for Hand Calculations & Automation

Document Version: 1.0 | Generated: 2026-04-25

# TABLE OF CONTENTS

1. System Base Values and Per-Unit Conversion

2. Admittance Matrix (Ybus) Construction

2.1 Transmission Line π-Model

2.2 Transformer Model

2.3 Complete Ybus Assembly Algorithm

3. Power Injection Calculations

3.1 Complex Power from Voltage

3.2 Bus Power Balance Equations

4. Branch Flow Calculations

4.1 Transmission Line Bidirectional Flows

4.2 Transformer Bidirectional Flows

4.3 Loss Calculations

5. Loading and Rating Calculations

6. Shunt Compensation Calculations

7. Complete Calculation Workflow

8. Hand Calculation Example

9. Automation Code Template

# 1. SYSTEM BASE VALUES AND PER-UNIT CONVERSION

## 1.1 Base Values Definition

The per-unit system normalizes all electrical quantities:

Base MVA (Sbase) = Given in input (typically 100 MVA)
Base Voltage (Vbase_kV) = Given per bus (e.g., 132 kV, 33 kV, 11 kV)
Base Current (Ibase) = Sbase / (√3 × Vbase_kV)
Base Impedance (Zbase) = Vbase_kV² / Sbase

## 1.2 Per-Unit Conversion Formulas

| Quantity | Actual Value | Per-Unit Value |
| --- | --- | --- |
| Voltage | V_kV | V_pu = V_kV / Vbase_kV |
| Current | I_A | I_pu = I_A / Ibase |
| Impedance | Z_Ω | Z_pu = Z_Ω / Zbase |
| Power | S_MVA | S_pu = S_MVA / Sbase |
| Reactive Power | Q_Mvar | Q_pu = Q_Mvar / Sbase |

## 1.3 Input Data Per-Unit Values

The input file provides impedance values already in per-unit on system base:

LINE_DATA format: [line_num, name, from_bus, to_bus, length_km, 
                 R_per_km, X_per_km, B_per_km, rateA_MVA, status, area, zone, owner]

Total Line Impedance (pu):
    R_total_pu = R_per_km × length_km
    X_total_pu = X_per_km × length_km  
    B_total_pu = B_per_km × length_km

TRANSFORMER_DATA format: [xfmr_num, name, from_bus, to_bus, R_pu, X_pu, 
                          tap_ratio, rateA_MVA, phase_shift_deg, ...]

Note: Transformer R and X are already total values in pu

# 2. ADMITTANCE MATRIX (Ybus) CONSTRUCTION

The Ybus matrix is the core of power flow calculations. It relates bus voltages to injected currents:

[I_bus] = [Ybus] × [V_bus]

Where:
    I_bus = Vector of bus injection currents (n×1 complex)
    V_bus = Vector of bus voltages (n×1 complex)
    Ybus  = Admittance matrix (n×n complex)
    n     = Number of buses

## 2.1 Transmission Line π-Model

Physical Model Diagram:

Bus i                              Bus j
           │                                 │
           ├──┬────── R+jX ──────┬───────────┤
           │  │                  │           │
          jB/2│                 jB/2         │
           │  │                  │           │
           └──┴──────────────────┴───────────┘
           
Where:
    R = Series resistance (pu)
    X = Series reactance (pu)
    B = Total line charging susceptance (pu)

Mathematical Derivation:

Step 1: Calculate series admittance
    Z_series = R + jX  (complex impedance)
    y_series = 1 / Z_series = 1 / (R + jX)
    
    Rationalize the denominator:
    y_series = (R - jX) / (R² + X²)
    
    Let D = R² + X²
    G_series = R / D      (series conductance)
    B_series = -X / D     (series susceptance)
    
    y_series = G_series + jB_series

Step 2: Shunt admittance (per side)
    y_shunt = j(B/2)      (purely reactive)

Step 3: Ybus contributions from this line
    Ybus[i][i] += y_series + j(B/2)   (diagonal element at bus i)
    Ybus[j][j] += y_series + j(B/2)   (diagonal element at bus j)
    Ybus[i][j] -= y_series             (off-diagonal element)
    Ybus[j][i] -= y_series             (off-diagonal element, symmetric)

## 2.2 Transformer Model

The transformer is modeled as an ideal transformer with series impedance:

Bus i (Primary)              Bus j (Secondary)
           │                              │
           │    ┌──────────────┐          │
           ├───┤  Tap Ratio a  ├──────────┤
           │    └──────┬───────┘          │
           │           │                  │
           │         R+jX                 │
           │           │                  │
           └───────────┴──────────────────┘
           
Where:
    a = tap_ratio (typically 0.9 to 1.1)
    R = Transformer resistance (pu)
    X = Transformer reactance (pu)

Mathematical Derivation:

Step 1: Calculate series admittance (same as line)
    Z_xfmr = R + jX
    y_series = 1 / (R + jX) = (R - jX) / (R² + X²)

Step 2: Ybus contributions with tap ratio
    Ybus[i][i] += y_series / a²         (primary side, adjusted by tap)
    Ybus[j][j] += y_series               (secondary side, no adjustment)
    Ybus[i][j] -= y_series / a           (off-diagonal, divided by tap)
    Ybus[j][i] -= y_series / a           (symmetric off-diagonal)

Key Insight: The tap ratio a affects only the primary side diagonal 
element and both off-diagonal elements. This asymmetry is what 
allows transformers to control voltage.

## 2.3 Complete Ybus Assembly Algorithm

ALGORITHM: Build Ybus Matrix
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━

INPUT:
    - n_buses: Number of buses
    - branches: List of {from_bus, to_bus, r, x, b, ratio}
    - bus_index_map: Dictionary mapping bus_num → matrix index

OUTPUT:
    - Ybus: n×n complex matrix

STEPS:
1. Initialize Ybus as n×n zero matrix (complex)
   
2. FOR EACH branch in branches:
   a. Get matrix indices:
      i = bus_index_map[from_bus]
      j = bus_index_map[to_bus]
   
   b. Calculate series admittance:
      Z = complex(r, x)
      IF Z ≠ 0:
         y = 1.0 / Z
      ELSE:
         SKIP this branch (invalid)
   
   c. IF branch.ratio == 0 (TRANSMISSION LINE):
      Ybus[i][i] += y + complex(0, b)
      Ybus[j][j] += y + complex(0, b)
      Ybus[i][j] -= y
      Ybus[j][i] -= y
   
   d. ELSE (TRANSFORMER):
      a = branch.ratio
      Ybus[i][i] += y / (a²)
      Ybus[j][j] += y
      Ybus[i][j] -= y / a
      Ybus[j][i] -= y / a

3. RETURN Ybus

Python Implementation:
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
import numpy as np

def build_ybus(n_buses, branches, bus_index_map):
    Ybus = np.zeros((n_buses, n_buses), dtype=complex)
    
    for branch in branches:
        i = bus_index_map[branch['from_bus']]
        j = bus_index_map[branch['to_bus']]
        r, x, b = branch['r'], branch['x'], branch['b']
        ratio = branch['ratio']
        
        z = complex(r, x)
        if z != 0:
            y = 1.0 / z
            
            if ratio == 0:  # Line
                Ybus[i][i] += y + complex(0, b)
                Ybus[j][j] += y + complex(0, b)
                Ybus[i][j] -= y
                Ybus[j][i] -= y
            else:  # Transformer
                Ybus[i][i] += y / (ratio ** 2)
                Ybus[j][j] += y
                Ybus[i][j] -= y / ratio
                Ybus[j][i] -= y / ratio
    
    return Ybus

# 3. POWER INJECTION CALCULATIONS

## 3.1 Complex Power from Voltage and Current

FUNDAMENTAL EQUATION:
    S = V × I*

Where:
    S = Complex power (VA)
    V = Complex voltage (V)
    I* = Complex conjugate of current (A)

In Per-Unit:
    S_pu = V_pu × I_pu*

From Ybus:
    I = Ybus × V

Therefore:
    S = V × (Ybus × V)* = V × Ybus* × V*

For bus k:
    S_k = V_k × Σ(j=1 to n) [Y_kj* × V_j*]

Expanding into real and imaginary:
    S_k = P_k + jQ_k

Where:
    P_k = Real part of S_k (active power)
    Q_k = Imaginary part of S_k (reactive power)

## 3.2 Detailed Power Equations

For bus k with voltage V_k = |V_k|∠δ_k:

P_k = |V_k| × Σ(j=1 to n) |V_j| × |Y_kj| × cos(δ_k - δ_j - θ_kj)

Q_k = |V_k| × Σ(j=1 to n) |V_j| × |Y_kj| × sin(δ_k - δ_j - θ_kj)

Where:
    |V_k| = Voltage magnitude at bus k (pu)
    δ_k   = Voltage angle at bus k (radians)
    |Y_kj| = Magnitude of admittance element Y_kj
    θ_kj   = Angle of admittance element Y_kj

Alternative Matrix Form (used in code):
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
Given:
    V_complex = V_mag × exp(j × V_angle_rad)

Calculate:
    I_injection = Ybus @ V_complex      (matrix multiplication)
    S_complex = V_complex × conj(I_injection)
    
    P = real(S_complex)                 (active power, pu)
    Q = imag(S_complex)                 (reactive power, pu)
    
Convert to MW/Mvar:
    P_MW = P_pu × Sbase_MVA
    Q_Mvar = Q_pu × Sbase_MVA

SIGN CONVENTION:
    Positive P, Q → Power flowing INTO the bus (generation)
    Negative P, Q → Power flowing OUT of bus (load)

## 3.3 Python Implementation

def calculate_power_injection(Ybus, V_mag, V_angle_deg, baseMVA):
    """
    Calculate power injection at all buses
    
    Parameters:
        Ybus: n×n complex admittance matrix
        V_mag: array of voltage magnitudes (pu)
        V_angle_deg: array of voltage angles (degrees)
        baseMVA: system base MVA
    
    Returns:
        P_MW: array of active power injections (MW)
        Q_Mvar: array of reactive power injections (Mvar)
    """
    # Convert angle to radians
    V_angle_rad = np.radians(V_angle_deg)
    
    # Form complex voltage vector
    V_complex = V_mag * np.exp(1j * V_angle_rad)
    
    # Calculate injected current
    I_inj = Ybus @ V_complex
    
    # Calculate complex power: S = V × I*
    S = V_complex * np.conj(I_inj)
    
    # Extract real and imaginary parts
    P_pu = S.real
    Q_pu = S.imag
    
    # Convert to MW and Mvar
    P_MW = P_pu * baseMVA
    Q_Mvar = Q_pu * baseMVA
    
    return P_MW, Q_Mvar

# 4. BRANCH FLOW CALCULATIONS

## 4.1 Transmission Line Bidirectional Flows

PHYSICAL MODEL (π-model):
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
        Bus i                              Bus j
           │                                 │
           ├──┬────── y ──────┬─────────────┤
           │  │               │             │
         jB/2│              jB/2           │
           │  │               │             │
           └──┴───────────────┴─────────────┘

Where:
    y = 1/(R+jX) = series admittance
    B = total line charging susceptance

FORWARD FLOW (i → j):
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
Current through series element (i to j):
    I_series_ij = (V_i - V_j) × y

Shunt charging current at bus i:
    I_shunt_i = V_i × j(B/2)

Total current leaving bus i:
    I_from_i = I_series_ij + I_shunt_i
    I_from_i = (V_i - V_j) × y + V_i × j(B/2)

Complex power from bus i:
    S_ij = V_i × I_from_i*
    S_ij = V_i × [(V_i - V_j) × y + V_i × j(B/2)]*

REVERSE FLOW (j → i):
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
Current through series element (j to i):
    I_series_ji = (V_j - V_i) × y

Shunt charging current at bus j:
    I_shunt_j = V_j × j(B/2)

Total current leaving bus j:
    I_from_j = I_series_ji + I_shunt_j

Complex power from bus j:
    S_ji = V_j × I_from_j*

POWER LOSSES:
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
Total losses = S_ij + S_ji
(Note: This is positive for real power loss)

Loss_MW = real(S_ij + S_ji) × baseMVA
Loss_Mvar = imag(S_ij + S_ji) × baseMVA

## 4.2 Transformer Bidirectional Flows

TRANSFORMER MODEL:
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
        Bus i (Primary, tap side)      Bus j (Secondary)
           │                              │
           │    ┌──────────────┐          │
           ├───┤  Tap Ratio a  ├──────────┤
           │    └──────┬───────┘          │
           │           │                  │
           │           y                  │
           │           │                  │
           └───────────┴──────────────────┘

Where:
    a = tap_ratio
    y = 1/(R+jX) = series admittance

FORWARD FLOW (i → j):
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
Current through transformer (accounting for tap):
    I_fwd = (V_i/a - V_j) × y

Complex power leaving bus i:
    S_fwd = V_i × I_fwd*
    S_fwd = V_i × [(V_i/a - V_j) × y]*

REVERSE FLOW (j → i):
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
Current from secondary side (accounting for tap):
    I_rev = (V_j × a - V_i) × (y / a²)

Complex power leaving bus j:
    S_rev = V_j × I_rev*
    S_rev = V_j × [(V_j × a - V_i) × (y / a²)]*

POWER LOSSES:
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
Loss = S_fwd + S_rev
Loss_MW = real(S_fwd + S_rev) × baseMVA

IMPORTANT: The asymmetry in forward/reverse equations is due 
to the tap ratio being on the primary side.

## 4.3 Complete Python Implementation

def calculate_branch_flows(Ybus, branches, bus_index_map, 
                           V_mag, V_angle_deg, baseMVA):
    """
    Calculate bidirectional power flows on all branches
    
    Returns: List of flow dictionaries for each branch
    """
    V_angle_rad = np.radians(V_angle_deg)
    V_complex = V_mag * np.exp(1j * V_angle_rad)
    
    flows = []
    
    for branch in branches:
        i = bus_index_map[branch['from_bus']]
        j = bus_index_map[branch['to_bus']]
        V_i = V_complex[i]
        V_j = V_complex[j]
        
        r, x, b = branch['r'], branch['x'], branch['b']
        ratio = branch['ratio']
        rateA = branch.get('rateA', 9999)
        
        z = complex(r, x)
        y = 1.0 / z if z != 0 else 0
        
        if ratio == 0:  # TRANSMISSION LINE
            # Forward flow (from_bus → to_bus)
            I_series = (V_i - V_j) * y
            I_shunt = V_i * complex(0, b/2)
            S_fwd = V_i * np.conj(I_series + I_shunt)
            
            # Reverse flow (to_bus → from_bus)
            I_series_rev = (V_j - V_i) * y
            I_shunt_rev = V_j * complex(0, b/2)
            S_rev = V_j * np.conj(I_series_rev + I_shunt_rev)
            
        else:  # TRANSFORMER
            # Forward flow
            I_fwd = (V_i / ratio - V_j) * y
            S_fwd = V_i * np.conj(I_fwd)
            
            # Reverse flow
            I_rev = (V_j * ratio - V_i) * (y / ratio**2)
            S_rev = V_j * np.conj(I_rev)
        
        losses = S_fwd + S_rev
        MVA_fwd = abs(S_fwd) * baseMVA
        loading = (MVA_fwd / rateA * 100) if rateA > 0 else 0
        
        flows.append({
            'from_bus': branch['from_bus'],
            'to_bus': branch['to_bus'],
            'P_fwd_MW': S_fwd.real * baseMVA,
            'Q_fwd_Mvar': S_fwd.imag * baseMVA,
            'P_rev_MW': S_rev.real * baseMVA,
            'Q_rev_Mvar': S_rev.imag * baseMVA,
            'losses_MW': losses.real * baseMVA,
            'MVA_fwd': MVA_fwd,
            'loading_pct': loading,
            'tap_ratio': ratio if ratio != 0 else None
        })
    
    return flows

# 5. LOADING AND RATING CALCULATIONS

LINE LOADING PERCENTAGE:
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━

Step 1: Calculate apparent power (MVA)
    P_fwd = |P_fwd_MW|           (absolute value)
    Q_fwd = |Q_fwd_Mvar|         (absolute value)
    MVA_flow = √(P_fwd² + Q_fwd²)

Step 2: Get rating
    rateA = Line rating from input (MVA)
    If rateA = 0, set to 9999 (no limit)

Step 3: Calculate loading percentage
    Loading_% = (MVA_flow / rateA) × 100

Step 4: Status determination
    IF Loading_% > 100:    Status = "OVERLOADED"
    ELIF Loading_% > 80:   Status = "HIGH"
    ELIF Loading_% > 60:   Status = "MODERATE"
    ELSE:                  Status = "NORMAL"

TRANSFORMER LOADING:
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
Same formula applies, but use transformer rateA:
    Loading_% = (MVA_fwd / Xfmr_rateA) × 100

TAP POSITION CALCULATION:
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
Given:
    tap_ratio = Current tap ratio (e.g., 1.025)
    min_tap = Minimum tap (e.g., 0.9)
    step_size = Tap step size (e.g., 0.0125)

Calculate:
    tap_position = (tap_ratio - min_tap) / step_size
    tap_step = int(tap_position)

Example:
    tap_ratio = 1.025, min_tap = 0.9, step_size = 0.0125
    tap_step = (1.025 - 0.9) / 0.0125 = 10
    → Transformer is at tap position 10

# 6. SHUNT COMPENSATION CALCULATIONS

CAPACITOR BANK OUTPUT:
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
Given:
    Q_rated = Rated reactive power at nominal voltage (Mvar)
    V_actual = Actual bus voltage (pu)

Actual output (varies with V²):
    Q_actual = Q_rated × V_actual²

Reason: Capacitor impedance Z_c = 1/(jωC) is constant
        Current I = V/Z_c = V × jωC
        Power Q = V × I = V² × ωC ∝ V²

REACTOR OUTPUT:
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
Same formula applies (reactor absorbs reactive power):
    Q_absorbed = Q_rated × V_actual²

CONVERSION FROM BUS SHUNT DATA:
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
In PYPOWER format, bus shunt is in pu on system base:
    B_shunt_pu = Value from bus data column 5

If B_shunt_pu < 0:  → Capacitor (negative susceptance = capacitive)
    Q_cap_Mvar = |B_shunt_pu| × baseMVA

If B_shunt_pu > 0:  → Reactor (positive susceptance = inductive)
    Q_react_Mvar = |B_shunt_pu| × baseMVA

# 7. COMPLETE CALCULATION WORKFLOW

STEP-BY-STEP CALCULATION PROCEDURE:
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━

┌─────────────────────────────────────────────────────────┐
│ STEP 1: DATA PREPARATION                                │
├─────────────────────────────────────────────────────────┤
│ • Read input file (BUS_DATA, LINE_DATA, etc.)          │
│ • Extract baseMVA (typically 100)                       │
│ • Build bus_index_map: {bus_num → 0,1,2,...}          │
│ • Calculate line totals: R×L, X×L, B×L                 │
└─────────────────────────────────────────────────────────┘
                           ↓
┌─────────────────────────────────────────────────────────┐
│ STEP 2: BUILD YBUS MATRIX                              │
├─────────────────────────────────────────────────────────┤
│ • Initialize n×n zero matrix (complex)                 │
│ • For each branch:                                      │
│   - Calculate y = 1/(R+jX)                             │
│   - If line: Add y±jB to diagonals, -y to off-diag    │
│   - If transformer: Adjust by tap ratio a              │
└─────────────────────────────────────────────────────────┘
                           ↓
┌─────────────────────────────────────────────────────────┐
│ STEP 3: FORM VOLTAGE VECTOR                            │
├─────────────────────────────────────────────────────────┤
│ • V_mag[i] = Voltage magnitude at bus i (pu)           │
│ • V_angle[i] = Voltage angle at bus i (degrees)        │
│ • V_complex = V_mag × exp(j × radians(V_angle))        │
└─────────────────────────────────────────────────────────┘
                           ↓
┌─────────────────────────────────────────────────────────┐
│ STEP 4: CALCULATE BUS INJECTIONS                       │
├─────────────────────────────────────────────────────────┤
│ • I_inj = Ybus × V_complex                             │
│ • S = V_complex × conj(I_inj)                          │
│ • P_MW = real(S) × baseMVA                             │
│ • Q_Mvar = imag(S) × baseMVA                           │
└─────────────────────────────────────────────────────────┘
                           ↓
┌─────────────────────────────────────────────────────────┐
│ STEP 5: CALCULATE BRANCH FLOWS                         │
├─────────────────────────────────────────────────────────┤
│ • For each line:                                        │
│   - Forward: S_fwd = Vi × [(Vi-Vj)×y + Vi×jB/2]*      │
│   - Reverse: S_rev = Vj × [(Vj-Vi)×y + Vj×jB/2]*      │
│ • For each transformer:                                 │
│   - Forward: S_fwd = Vi × [(Vi/a - Vj)×y]*             │
│   - Reverse: S_rev = Vj × [(Vj×a - Vi)×(y/a²)]*       │
│ • Losses = S_fwd + S_rev                               │
│ • Loading = |S_fwd| × baseMVA / rateA × 100            │
└─────────────────────────────────────────────────────────┘
                           ↓
┌─────────────────────────────────────────────────────────┐
│ STEP 6: PROCESS SHUNTS                                 │
├─────────────────────────────────────────────────────────┤
│ • Capacitor: Q_out = Q_rated × V²                      │
│ • Reactor: Q_abs = Q_rated × V²                        │
└─────────────────────────────────────────────────────────┘
                           ↓
┌─────────────────────────────────────────────────────────┐
│ STEP 7: VALIDATE & OUTPUT                              │
├─────────────────────────────────────────────────────────┤
│ • Check for NaN/Inf values                              │
│ • Check voltage limits (0.85 - 1.15 pu)                │
│ • Generate output files (CSV, PY, TXT)                 │
└─────────────────────────────────────────────────────────┘

# 8. HAND CALCULATION EXAMPLE

Example: 3-Bus System

SYSTEM DATA:
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
Base MVA = 100

Bus Data:
  Bus 1: V = 1.05∠0° pu (Slack), base_kV = 132
  Bus 2: V = 1.00∠?° pu (PQ), base_kV = 132
  Bus 3: V = 1.00∠?° pu (PQ), base_kV = 33

Line Data:
  Line 1-2: R=0.02, X=0.06, B=0.06 pu
  Line 1-3: R=0.08, X=0.24, B=0.05 pu (via transformer)
  Line 2-3: R=0.06, X=0.18, B=0.04 pu

Transformer (Line 1-3 has tap ratio):
  Tap ratio = 0.95 (step-down from 132kV to 33kV)

━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
STEP 1: Calculate series admittances
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━

Line 1-2: Z = 0.02 + j0.06
  D = 0.02² + 0.06² = 0.004
  y₁₂ = (0.02 - j0.06) / 0.004 = 5 - j15

Line 1-3: Z = 0.08 + j0.24
  D = 0.08² + 0.24² = 0.064
  y₁₃ = (0.08 - j0.24) / 0.064 = 1.25 - j3.75

Line 2-3: Z = 0.06 + j0.18
  D = 0.06² + 0.18² = 0.036
  y₂₃ = (0.06 - j0.18) / 0.036 = 1.667 - j5.0

━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
STEP 2: Build Ybus (3×3 matrix)
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━

Y₁₁ = y₁₂ + j(0.06/2) + y₁₃/(0.95²) + j(0.05/2)
     = (5-j15) + j0.03 + (1.25-j3.75)/0.9025 + j0.025
     = 5 + 1.385 + j(-15 + 0.03 - 4.155 + 0.025)
     = 6.385 - j19.1

Y₂₂ = y₁₂ + j(0.06/2) + y₂₃ + j(0.04/2)
     = (5-j15) + j0.03 + (1.667-j5.0) + j0.02
     = 6.667 - j19.95

Y₃₃ = y₁₃ + j(0.05/2) + y₂₃ + j(0.04/2)
     = (1.25-j3.75) + j0.025 + (1.667-j5.0) + j0.02
     = 2.917 - j8.705

Y₁₂ = Y₂₁ = -y₁₂ = -5 + j15

Y₁₃ = -y₁₃/0.95 = -(1.25-j3.75)/0.95 = -1.316 + j3.947

Y₂₃ = Y₃₂ = -y₂₃ = -1.667 + j5.0

Ybus = | 6.385-j19.1   -5+j15       -1.316+j3.947 |
       | -5+j15         6.667-j19.95 -1.667+j5.0   |
       | -1.316+j3.947  -1.667+j5.0   2.917-j8.705 |

━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
STEP 3: Calculate power injection at Bus 1 (given V)
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━

Assume V₂ = 1.00∠-2° pu, V₃ = 0.98∠-5° pu (from power flow)

V = [1.05∠0°, 1.00∠-2°, 0.98∠-5°]

Convert to rectangular:
V₁ = 1.05 + j0
V₂ = 0.9994 - j0.0349
V₃ = 0.9763 - j0.0854

I₁ = Y₁₁×V₁ + Y₁₂×V₂ + Y₁₃×V₃
   = (6.385-j19.1)(1.05) + (-5+j15)(0.9994-j0.0349) + ...
   
S₁ = V₁ × I₁* = P₁ + jQ₁

(Continue calculation for all buses...)

━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━
STEP 4: Calculate line flow 1→2
━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━━

I_series = (V₁ - V₂) × y₁₂ = (1.05+j0 - 0.9994-j0.0349) × (5-j15)
         = (0.0506 + j0.0349) × (5-j15)

I_shunt = V₁ × j(B/2) = (1.05) × j(0.03) = j0.0315

S₁₂ = V₁ × (I_series + I_shunt)*

This gives P_fwd and Q_fwd in pu. Multiply by 100 for MW/Mvar.

# 9. COMPLETE AUTOMATION CODE TEMPLATE

"""
Standalone Power Flow Calculator
Copy this code to create your own power flow tool
"""

import numpy as np

class PowerFlowCalculator:
    def __init__(self, baseMVA=100.0):
        self.baseMVA = baseMVA
        self.Ybus = None
        self.bus_index_map = {}
        self.n_buses = 0
        
    def load_system(self, buses, branches):
        """
        buses: dict {bus_num: {'V_init': float, 'angle_init': float, 'base_kV': float}}
        branches: list of dict {from_bus, to_bus, r, x, b, ratio, rateA}
        """
        self.buses = buses
        self.branches = branches
        self.n_buses = len(buses)
        self.bus_index_map = {b: i for i, b in enumerate(sorted(buses.keys()))}
        self._build_ybus()
        
    def _build_ybus(self):
        self.Ybus = np.zeros((self.n_buses, self.n_buses), dtype=complex)
        for br in self.branches:
            i = self.bus_index_map[br['from_bus']]
            j = self.bus_index_map[br['to_bus']]
            z = complex(br['r'], br['x'])
            if z == 0: continue
            y = 1.0 / z
            if br['ratio'] == 0:  # Line
                self.Ybus[i,i] += y + complex(0, br['b'])
                self.Ybus[j,j] += y + complex(0, br['b'])
                self.Ybus[i,j] -= y
                self.Ybus[j,i] -= y
            else:  # Transformer
                a = br['ratio']
                self.Ybus[i,i] += y / (a**2)
                self.Ybus[j,j] += y
                self.Ybus[i,j] -= y / a
                self.Ybus[j,i] -= y / a
    
    def solve(self, V_mag=None, V_angle=None):
        """Solve power flow for given voltages"""
        if V_mag is None:
            V_mag = np.array([self.buses[b]['V_init'] 
                             for b in sorted(self.buses.keys())])
        if V_angle is None:
            V_angle = np.array([self.buses[b]['angle_init'] 
                               for b in sorted(self.buses.keys())])
        
        V_rad = np.radians(V_angle)
        V = V_mag * np.exp(1j * V_rad)
        I = self.Ybus @ V
        S = V * np.conj(I)
        
        results = {
            'P_MW': S.real * self.baseMVA,
            'Q_Mvar': S.imag * self.baseMVA,
            'V_pu': V_mag,
            'V_angle_deg': V_angle,
            'branches': self._calc_flows(V)
        }
        return results
    
    def _calc_flows(self, V):
        flows = []
        for br in self.branches:
            i = self.bus_index_map[br['from_bus']]
            j = self.bus_index_map[br['to_bus']]
            Vi, Vj = V[i], V[j]
            y = 1.0 / complex(br['r'], br['x'])
            
            if br['ratio'] == 0:  # Line
                Ish = Vi * complex(0, br['b']/2)
                S_fwd = Vi * np.conj((Vi-Vj)*y + Ish)
                Ish_j = Vj * complex(0, br['b']/2)
                S_rev = Vj * np.conj((Vj-Vi)*y + Ish_j)
            else:  # Transformer
                a = br['ratio']
                S_fwd = Vi * np.conj((Vi/a - Vj)*y)
                S_rev = Vj * np.conj((Vj*a - Vi)*(y/a**2))
            
            MVA = abs(S_fwd) * self.baseMVA
            rateA = br.get('rateA', 9999)
            
            flows.append({
                'from': br['from_bus'], 'to': br['to_bus'],
                'P_fwd_MW': S_fwd.real * self.baseMVA,
                'Q_fwd_Mvar': S_fwd.imag * self.baseMVA,
                'P_rev_MW': S_rev.real * self.baseMVA,
                'Q_rev_Mvar': S_rev.imag * self.baseMVA,
                'loss_MW': (S_fwd + S_rev).real * self.baseMVA,
                'MVA': MVA,
                'loading_%': MVA/rateA*100 if rateA > 0 else 0
            })
        return flows


# USAGE EXAMPLE
if __name__ == "__main__":
    pf = PowerFlowCalculator(baseMVA=100)
    
    # Define system
    buses = {
        1: {'V_init': 1.05, 'angle_init': 0, 'base_kV': 132},
        2: {'V_init': 1.00, 'angle_init': -2, 'base_kV': 132},
        3: {'V_init': 0.98, 'angle_init': -5, 'base_kV': 33}
    }
    
    branches = [
        {'from_bus': 1, 'to_bus': 2, 'r': 0.02, 'x': 0.06, 'b': 0.06, 'ratio': 0, 'rateA': 100},
        {'from_bus': 1, 'to_bus': 3, 'r': 0.08, 'x': 0.24, 'b': 0.05, 'ratio': 0.95, 'rateA': 50},
        {'from_bus': 2, 'to_bus': 3, 'r': 0.06, 'x': 0.18, 'b': 0.04, 'ratio': 0, 'rateA': 80}
    ]
    
    pf.load_system(buses, branches)
    results = pf.solve()
    
    print("Bus Injections:")
    for i, bus in enumerate(sorted(buses.keys())):
        print(f"  Bus {bus}: P={results['P_MW'][i]:.2f} MW, Q={results['Q_Mvar'][i]:.2f} Mvar")
    
    print("\nBranch Flows:")
    for f in results['branches']:
        print(f"  {f['from']}→{f['to']}: P={f['P_fwd_MW']:.2f} MW, Loading={f['loading_%']:.1f}%")